## How to use the SCOP tool
One tab per climate
For each tab
From row 1 to 30 : Input data for SCOP
From 1 to 25 : Input for SEER
All coloured cells shall be filled in, because they are used for the calculations.
All grey cells are optional to fill in ; they provide information on the unit for which the calculation is made
Some cells shall be filled in by using a selected list of options
Calculate / Reset
To launch the calculations, click on "Calculate" button
To reset all calculations, click on "Reset" button : all input data and calculations will be reset
It is not needed to reset all the data to run a calculation, if needed, you can only change a data and click on "Calculate"
Bin calculation
Cells of columns B to D are blocked and values cannot be changed
Results : Energy efficiency
The final results are : SCOPon, SCOP, hs according to ErP regulation
Error messages
In case of error in input data, an error message will appear, once the calculation is launched by clicking on Calculate"
Correct the data and click again on "Calculate"
This tool has been developed by CETIAT by the use of Microsoft Excel version14.0.7237.5000 (32 bits). The tool shall be used by the empowered certification bodies of the Heat Pump Keymark product certification scheme and maybe used by manufacturers in order to calculate their performance in a consistence with the certification bodies. Neither the developer nor the Heat Pump Keymark may be held responsible for any errors that may occur from the use of the tool.
Version date: 2021_05_11 (V7)
For T<Tbiv, verification that for T<Tbiv Pdh is not higher than the heating load
In cooling mode: declared cooling capacity cannot be lower than 10% of the cooling load
Cdc is given with 4 digit instead of 3 (3 digits after the coma)
Version date: 2021_02_02 (V6)
Cdh is given with 4 digit instead of 3 (3 digits after the coma)
Version date: 2020_12_17
Automatic control that Tbiv and TOL are integers
Automatic control that for T>=Tbiv the declared capacity is not below 0,9xheating load value
If declared TOL<Tdesignh, E condition corresponds to Tdesignh
Version date: 2020_11_18
Pdesignh replaced by Prated
E definition extended to E(TOL) or E(Tdesignh)
Modification of the programs to make it possible to redo the calculation after some data to entry have been changed, without reseting all the data.
Version date: 2020_03_24
Correction of the formula to calcuale EERbin (formula 10 in EN 14825:2018)
12/7°C | fixed | outdoor air-to-water
23/18°C | variable | exhaust air-to-water
water-to-water
35°C | fixed | brine-to-water
55°C | staged | DX-to-water
variable
heating only |  | electricity
reversible |  | fossil fuel

## SCOP water_based HP average
Calculation of energy efficiency - Average climate
Product reference |  |  | Reference conditions
Manufacturer |  |  | Climate | average
Product reference |  |  | Tdesignh | -10 | °C
Type of heat pump |  |  | Prated | 20 | kW
Operating mode | heating only |  | Tbiv | 0 | °C
Temperature application | 55°C |  | TOL | -8 | °C |  | Energy Efficiency
Water flow | fixed |  | HHE | 2066 | hours |  | SCOPon | SCOP | hs | QHE (kWh)
Water outlet temperature | fixed |  | QH | 41320 | kWh |  | 2.5436 | 2.5424 | 98.6977 | 16252.0862
Capacity control | variable |  | Fossil fuel backup efficiency | - | %
Backup heater | electricity
Performance data
Condition | Outdoor air T°C | Part load ratio (%) | Part Load (kW) | Inlet / outlet water temperatures for testing | Declared Capacity (kW) | Declared COPd | Cdh | CR | COPbin
A | -7 | 88.4615 | 17.6923 |  | 16 | 3 | 0.9 | 1 | 3 |  | 9.55 | 16
B | 2 | 53.8462 | 10.7692 |  | 20 | 3 | 0.9 | 0.53846 | 2.7632 |  | 11.17 | 20
C | 7 | 34.6154 | 6.9231 |  | 20 | 3 | 0.9 | 0.34615 | 2.5234 |  | 12.66 | 20
D | 12 | 15.3846 | 3.0769 |  | 20 | 3 | 0.9 | 0.15385 | 1.9355 |  | 14.3 | 20
E(TOL) or E(Tdesignh) | -8 | 92.3077 | 18.4615 |  | 10 | 3 | 0.9 | 1 | 3 |  | 7.8 | 10
F(Tbiv) | 0 | 61.5385 | 12.3077 |  | 12 | 3 | 0.9 | 1 | 3 |  | 9.6969 | 12.3077
Auxiliairy power consumptions
Operating modes for heating only |  |  |  |  | Operating modes for reversible units
| Hours | Power input (W) | P * h (kWh) |  |  | Hours | Power input (W) | P * h (kWh)
Thermostat off | 178 | 1 | 0.178 |  | Thermostat off | 178
Stand by | 0 | 1 | 0 |  | Stand by | 0
Off mode | 3672 | 1 | 3.672 |  | Off mode | 0
Cranckase heater | 3850 | 1 | 3.85 |  | Cranckase heater | 178
Bin calculation
Condition | Bin | Outdoor air temp. | Hours | Part load ratio | Heat demand (kW) | Hea load covered by the heat pump |  | Back up heater | Annual heating demand | Annual energy consumption
| j | Tj | hj |  | Ph(tj) |  | COPbin(Tj) | elbu(Tj) | hj * Ph(Tj)
| - | °C | -
| 21 | -10 | 1 | 100 | 20 | - | - | 20 | 20 | 20
| 22 | -9 | 25 | 96.1538 | 19.2308 | - | - | 19.2308 | 480.7692 | 480.7692
TOL | 23 | -8 | 23 | 92.3077 | 18.4615 | 10 | 3 | 8.4615 | 424.6154 | 271.2821
-7 | 24 | -7 | 24 | 88.4615 | 17.6923 | 16 | 3 | 1.6923 | 424.6154 | 168.6154
| 25 | -6 | 27 | 84.6154 | 16.9231 | 15.4725 | 3 | 1.4505 | 456.9231 | 178.4176
| 26 | -5 | 68 | 80.7692 | 16.1538 | 14.9451 | 3 | 1.2088 | 1098.4615 | 420.9524
| 27 | -4 | 91 | 76.9231 | 15.3846 | 14.4176 | 3 | 0.96703 | 1400 | 525.3333
| 28 | -3 | 89 | 73.0769 | 14.6154 | 13.8901 | 3 | 0.72527 | 1300.7692 | 476.6227
| 29 | -2 | 165 | 69.2308 | 13.8462 | 13.3626 | 3 | 0.48352 | 2284.6154 | 814.7253
| 30 | -1 | 173 | 65.3846 | 13.0769 | 12.8352 | 3 | 0.24176 | 2262.3077 | 781.9853
Tbiv | 31 | 0 | 240 | 61.5385 | 12.3077 | 12.3077 | 3 | 0 | 2953.8462 | 984.6154
| 32 | 1 | 280 | 57.6923 | 11.5385 | 16.1538 | 2.8816 | 0 | 3230.7692 | 1121.1802
2 | 33 | 2 | 320 | 53.8462 | 10.7692 | 20 | 2.7632 | 0 | 3446.1538 | 1247.1795
| 34 | 3 | 357 | 50 | 10 | 20 | 2.7152 | 0 | 3570 | 1314.8207
| 35 | 4 | 356 | 46.1538 | 9.2308 | 20 | 2.6672 | 0 | 3286.1538 | 1232.0426
| 36 | 5 | 303 | 42.3077 | 8.4615 | 20 | 2.6193 | 0 | 2563.8462 | 978.8355
| 37 | 6 | 330 | 38.4615 | 7.6923 | 20 | 2.5713 | 0 | 2538.4615 | 987.22
7 | 38 | 7 | 326 | 34.6154 | 6.9231 | 20 | 2.5234 | 0 | 2256.9231 | 894.4103
| 39 | 8 | 348 | 30.7692 | 6.1538 | 20 | 2.4058 | 0 | 2141.5385 | 890.1608
| 40 | 9 | 335 | 26.9231 | 5.3846 | 20 | 2.2882 | 0 | 1803.8462 | 788.3212
| 41 | 10 | 315 | 23.0769 | 4.6154 | 20 | 2.1706 | 0 | 1453.8462 | 669.7788
| 42 | 11 | 215 | 19.2308 | 3.8462 | 20 | 2.0531 | 0 | 826.9231 | 402.7759
12 | 43 | 12 | 169 | 15.3846 | 3.0769 | 20 | 1.9355 | 0 | 520 | 268.6667
| 44 | 13 | 151 | 11.5385 | 2.3077 | 20 | 1.8179 | 0 | 348.4615 | 191.6827
| 45 | 14 | 105 | 7.6923 | 1.5385 | 20 | 1.7003 | 0 | 161.5385 | 95.0041
| 46 | 15 | 74 | 3.8462 | 0.76923 | 20 | 1.5828 | 0 | 56.9231 | 35.9645
|  |  | 4910 | [5 empty] | 41312.3077 | 16241.3621
Calculate
Reset

## SCOP water_based HP warmer
Calculation of energy efficiency - Warmer climate
Product designation |  |  | Reference conditions
Manufacturer |  |  | Climate | warmer
Product reference |  |  | Tdesignh | 2 | °C
Type of heat pump | outdoor air-to-water |  | Prated |  | kW
Operating mode | heating only |  | Tbiv |  | °C
Temperature application | 35°C |  | TOL |  | °C |  | Energy Efficiency
Water flow | fixed |  | HHE | 1336 | hours |  | SCOPon | SCOP | hs | QHE (kWh)
Water outlet temperature | fixed |  | QH |  | kWh
Capacity control | fixed |  | Fossil fuel backup efficiency |  | %
Backup heater | electricity
Performance data
Condition | Outdoor air T°C | Part load ratio (%) | Part Load (kW) | Inlet / outlet water temperatures for testing | Declared Capacity (kW) | Declared COPd | Cdh | CR | COPbin
A | -7
B | 2 | [9 empty] | 12
C | 7 | [9 empty] | 12
D | 12 | [9 empty] | 12
E(TOL) or E(Tdesignh) | [10 empty] | 12
F(Tbiv) | [10 empty] | 12
Auxiliairy power consumptions
Operating modes for heating only |  |  |  |  | Operating modes for reversible units
| Hours | Power input (W) | P * h (kWh) |  |  | Hours | Power input (W) | P * h (kWh)
Thermostat off | 754 |  |  |  | Thermostat off | 754
Stand by | 0 |  |  |  | Stand by | 0
Off mode | 4416 |  |  |  | Off mode | 0
Cranckase heater | 5170 |  |  |  | Cranckase heater | 754
Bin calculation
Condition | Bin | Outdoor air temperature | Hours | Part load ratio | Heat load (kW) | Hea load covered by the heat pump |  | Electric back up heater | Annual heating demand | Annual energy consumption
| j | Tj | hj | pl(Tj) | Ph(Tj) |  | COPbin(Tj) | elbu(Tj) | hj * Ph(Tj)
| - | °C | -
B | 33 | 2 | 3
| 34 | 3 | 22
| 35 | 4 | 63
| 36 | 5 | 63
| 37 | 6 | 175
C | 38 | 7 | 162
| 39 | 8 | 259
| 40 | 9 | 360
| 41 | 10 | 428
| 42 | 11 | 430
D | 43 | 12 | 503
| 44 | 13 | 444
| 45 | 14 | 384
| 46 | 15 | 294
3590
Calculate
Reset

## SCOP water_based HP colder
Calculation of energy efficiency - Colder climate
Product designation |  |  | Reference conditions
Manufacturer |  |  | Climate | colder
Product reference |  |  | Tdesignh | -22 | °C
Type of heat pump | outdoor air-to-water |  | Prated |  | kW
Operating mode | heating only |  | Tbiv |  | °C
Temperature application | 55°C |  | TOL |  | °C |  | Energy Efficiency
Water flow | fixed |  | HHE | 2465 | hours |  | SCOPon | SCOP | hs | QHE (kWh)
Water outlet temperature | fixed |  | QH |  | kWh
Capacity control | fixed |  | Fossil fuel backup efficiency |  | %
Backup heater | electricity
Performance data
Condition | Outdoor air T°C | Part load ratio % | Part load (kW) | Inlet/outlet water temperatures for testing | Declared Capacity (kW) | Declared COPd | Cdh | CR | COPbin
A | -7 | [9 empty] | 12
B | 2 | [9 empty] | 12
C | 7 | [9 empty] | 12
D | 12 | [9 empty] | 12
E(TOL) or E(Tdesignh) | [10 empty] | 14
F(Tbiv) | [10 empty] | 12
G | -15 | [9 empty] | 9
Auxiliary power consumptions
Operating modes for heating only |  |  |  |  | Operating modes for reversible units
| Hours | Power input (W) | P * h (kWh) |  |  | Hours | Power input (W) | P * h (kWh)
Thermostat off | 106 |  |  |  | Thermostat off | 106
Stand by | 0 |  |  |  | Stand by | 0
Off mode | 2208 |  |  |  | Off mode | 0
Cranckase heater | 2314 |  |  |  | Cranckase heater | 106
Bin calculation
Condition | Bin | Outdoor air temperature | Hours | Part load ratio | Heat load | Heat load covered by the heat pump |  | Electric back up heater | Annual heating demand | Annual energy consumption
| j | Tj | hj | pl(Tj) | Ph(Tj) |  | COPbin(Tj) | elbu(Tj) | hj * Ph(Tj)
| - | °C | - | % | kW | kW | -
| 9 | -22 | 1
| 10 | -21 | 6
| 11 | -20 | 13
| 12 | -19 | 17
| 13 | -18 | 19
| 14 | -17 | 26
| 15 | -16 | 39
G | 16 | -15 | 41
| 17 | -14 | 35
| 18 | -13 | 52
| 19 | -12 | 37
| 20 | -11 | 41
| 21 | -10 | 43
| 22 | -9 | 54
| 23 | -8 | 90
A | 24 | -7 | 125
| 25 | -6 | 169
| 26 | -5 | 195
| 27 | -4 | 278
| 28 | -3 | 306
| 29 | -2 | 454
| 30 | -1 | 385
| 31 | 0 | 490
| 32 | 1 | 533
B | 33 | 2 | 380
| 34 | 3 | 228
| 35 | 4 | 261
| 36 | 5 | 279
| 37 | 6 | 229
C | 38 | 7 | 269
| 39 | 8 | 233
| 40 | 9 | 230
| 41 | 10 | 243
| 42 | 11 | 191
D | 43 | 12 | 146
| 44 | 13 | 150
| 45 | 14 | 97
| 46 | 15 | 61
6446
Calculate
Reset

## SEER water_based HP
Calculation of energy efficiency of reversible water based heat pumps (SEER)
Product designation |  |  | Reference conditions
Manufacturer |  |  | Climate | average
Product reference |  |  | Tdesignc | 35 | °C
Type of heat pump | outdoor air-to-water |  | Pdesignc |  | kW
Operating mode | reversible |  | HCE | 600 | hours |  | Energy Efficiency
Capacity control | variable |  | QC |  | kWh |  | SEERon | SEER | QCE (kWh)
Performance data
Condition | Outdoor air T°C | Part load ratio (%) | Part Load (kW) | Declared Capacity (kW) | Declared EERd | Cdc | CR | EERbin
A | 35 | [8 empty] | 10
B | 30 | [8 empty] | 12
C | 25 | [8 empty] | 12
D | 20 | [8 empty] | 12
Auxiliary power consumptions
| Hours | Power input (W) | P * h (kWh)
Thermostat off | 659
Stand by | 1377
Off mode | 0
Cranckase heater | 2036
Bin calculation
Condition | Bin | Outdoor air temp. | Hours | Part load ratio | Cooling demand (kW) | Cooling capacity of the heat pump | EER | Annual cooling demand | Annual electricity consumption
| j |  |  |  | Pc(Tj) |  |  | hj*Pc(Tj) | hj*(Pc(Tj)/EER(Tj)
- | - | °C | - | % | kW | kW | - | kWh | kWh
| 1 | 17 | 205
| 2 | 18 | 227
| 3 | 19 | 225
D | 4 | 20 | 225
| 5 | 21 | 216
| 6 | 22 | 215
| 7 | 23 | 218
| 8 | 24 | 197
C | 9 | 25 | 178
| 10 | 26 | 158
| 11 | 27 | 137
| 12 | 28 | 109
| 13 | 29 | 88
B | 14 | 30 | 63
| 15 | 31 | 39
| 16 | 32 | 31
| 17 | 33 | 24
| 18 | 34 | 17
A | 19 | 35 | 13
| 20 | 36 | 9
| 21 | 37 | 4
| 22 | 38 | 3
| 23 | 39 | 1
| 24 | 40 | 0
2602
Calculate
Reset