## How to use the SCOP-SEER tool
One tab per climate and mode (heating /cooling)
For each tab
From row 1 to 29 : Input data
All bold cells are blocked and values cannot be changed
All grey cells are optional to fill in ; they provide information on the unit for which the calculation is made
All coloured cells shall be filled in, because they are used for the calculations.
Some cells shall be filled in by using a selected list of options
Calculate / Reset
To launch the calculations, click on "Calculate" button
To reset all calculations, click on "Reset" button : all input data and calculations will be reset
Bin calculation
Cells of columns B to D are blocked and values cannot be changed
Results : Energy efficiency
The final results are: SCOPon, SCOP according to ErP regulation
Error messages
In case of error in input data, an error message will appear, once the calculation is launched by clicking on "Calculate"
Correct the data and click again on "Calculate"
This tool has been developed by CETIAT by the use of Microsoft Excel version14.0.7237.5000 (32 bits). The tool shall be used by the empowered certification bodies of the Heat Pump Keymark product certification scheme and maybe used by manufacturers in order to calculate their performance in a consistence with the certification bodies. Neither the developer nor the Heat Pump Keymark may be held responsible for any errors that may occur from the use of the tool.
Version date: 2019-10-01
cooling only | fixed
reversible | variable
heating only | fixed
reversible | staged
variable

## SCOP air-air average
Calculation of energy efficiency of air-to-air heat pumps - Average climate
Product designation |  |  | Reference conditions
Manufacturer |  |  | Climate | average
Product reference |  |  | Tdesignh | -10 | °C
Type of heat pump | air-to-air |  | Pdesignh |  | kW
Operating mode | heating only |  | Tbiv |  | °C
Capacity control | variable |  | TOL |  | °C |  | Energy Efficiency
|  |  | HHE | 1400 | hours |  | SCOPon | SCOP | QHE (kWh)
|  |  | QH |  | kWh
Performance data
Condition | Outdoor air T°C | Part load ratio (%) | Part Load (kW) | Declared Capacity (kW) | Declared COPd | Cdh | CR | COPbin
A | -7 | [9 empty] | 10
B | 2 | [9 empty] | 10
C | 7 | [9 empty] | 10
D | 12 | [9 empty] | 10
E(TOL) | [10 empty] | 10
F(Tbiv) | [10 empty] | 10
Auxiliary power consumptions
Operating modes for heating only |  |  |  |  | Operating modes for reversible units
| Hours | Power input (W) | P * h (kWh) |  |  | Hours | Power input (W) | P * h (kWh)
Thermostat off | 179 |  |  |  | Thermostat off | 179
Stand by | 0 |  |  |  | Stand by | 0
Off mode | 3672 |  |  |  | Off mode | 0
Cranckase heater | 3851 |  |  |  | Cranckase heater | 179
Bin calculation
Condition | Bin | Outdoor air temp. | Hours | Part load ratio | Heat demand (kW) | Heating capacity of the heat pump | COP(Tj) | Electric back up heater | Annual heating demand | Annual electricity consumption with electrical back up heater
| j | Tj | hj |  | Ph(tj) |  |  | elbu(Tj) | hj * Ph(Tj) | hj*((Ph(Tj)-elbu(Tj))/ COP(Tj))+elbu(Tj))
- | - | °C | - | % | kW | kW | - | kW | kWh | kWh
| 21 | -10 | 1
| 22 | -9 | 25
| 23 | -8 | 23
A | 24 | -7 | 24
| 25 | -6 | 27
| 26 | -5 | 68
| 27 | -4 | 91
| 28 | -3 | 89
| 29 | -2 | 165
| 30 | -1 | 173
| 31 | 0 | 240
| 32 | 1 | 280
B | 33 | 2 | 320
| 34 | 3 | 357
| 35 | 4 | 356
| 36 | 5 | 303
| 37 | 6 | 330
C | 38 | 7 | 326
| 39 | 8 | 348
| 40 | 9 | 335
| 41 | 10 | 315
| 42 | 11 | 215
D | 43 | 12 | 169
| 44 | 13 | 151
| 45 | 14 | 105
| 46 | 15 | 74
4910
Calculate
Reset

## SCOP air-air warmer
Calculation of energy efficiency of air-to-air heat pumps - Warmer climate
Product designation |  |  | Reference conditions
Manufacturer |  |  | Climate | warmer
Product reference |  |  | Tdesignh | 2 | °C
Type of heat pump | air-to-air |  | Pdesignh |  | kW
Operating mode | reversible |  | Tbiv |  | °C
Capacity control | fixed |  | TOL |  | °C |  | Energy Efficiency
|  |  | HHE | 1400 | hours |  | SCOPon | SCOP | QHE (kWh)
|  |  | QH |  | kWh
Performance data
Condition | Outdoor air T°C | Part load ratio (%) | Part Load (kW) | Declared Capacity (kW) | Declared COPd | Cdh | CR | COPbin
A | -7
B | 2 | [9 empty] | 10 | 10
C | 7 | [9 empty] | 10 | 10
D | 12 | [9 empty] | 10 | 10
E(TOL) | [10 empty] | 10 | 10
F(Tbiv) | [10 empty] | 10 | 9.2857
Auxiliairy power consumptions
Operating modes for heating only |  |  |  |  | Operating modes for reversible units
| Hours | Power input (W) | P * h (kWh) |  |  | Hours | Power input (W) | P * h (kWh)
Thermostat off | 755 |  |  |  | Thermostat off | 755
Stand by | 0 |  |  |  | Stand by | 0
Off mode | 4345 |  |  |  | Off mode | 0
Cranckase heater | 4476 |  |  |  | Cranckase heater | 755
Bin calculation
Condition | Bin | Outdoor air temperature | Hours | Part load ratio | Heat load (kW) | Hea load covered by the heat pump |  | Electric back up heater | Annual heating demand | Annual electricity consumption with electrical back up heater
| j | Tj | hj | pl(Tj) | Ph(Tj) |  | COPbin(Tj) | elbu(Tj) | hj * Ph(Tj) | hj*((Ph(Tj)-elbu(Tj))/ COPbin(Tj))+elbu(Tj))
- | - | °C | - | % | kW | kW | - | kW | kWh | kWh
B | 33 | 2 | 3
| 34 | 3 | 22
| 35 | 4 | 63
| 36 | 5 | 63
| 37 | 6 | 175
C | 38 | 7 | 162
| 39 | 8 | 259
| 40 | 9 | 360
| 41 | 10 | 428
| 42 | 11 | 430
D | 43 | 12 | 503
| 44 | 13 | 444
| 45 | 14 | 384
| 46 | 15 | 294
3590
Calculate
Reset

## SCOP air-air colder
Calculation of energy efficiency of air-to-air heat pumps - Colder climate
Product designation |  |  | Reference conditions
Manufacturer |  |  | Climate | colder
Product reference |  |  | Tdesignh | -22 | °C
Type of heat pump | air-to-air |  | Pdesignh |  | kW
Operating mode | heating only |  | Tbiv |  | °C
Capacity control | fixed |  | TOL |  | °C |  | Energy Efficiency
|  |  | HHE | 2100 | hours |  | SCOPon | SCOP | QHE (kWh)
|  |  | QH |  | kWh
Performance data
Condition | Outdoor air T°C | Part load ratio % | Part load (kW) | Declared Capacity (kW) | Declared COPd | Cdh | CR | COPbin
A | -7 | [9 empty] | 10
B | 2 | [9 empty] | 10
C | 7 | [9 empty] | 10
D | 12 | [9 empty] | 10
E(TOL) | [10 empty] | 10
F(Tbiv) | [10 empty] | 10
G | -15 | [9 empty] | 10
Auxiliary power consumptions
Operating modes for heating only |  |  |  |  | Operating modes for reversible units
| Hours | Power input (W) | P * h (kWh) |  |  | Hours | Power input (W) | P * h (kWh)
Thermostat off | 131 |  |  |  | Thermostat off | 131
Stand by | 0 |  |  |  | Stand by | 0
Off mode | 2189 |  |  |  | Off mode | 0
Cranckase heater | 2944 |  |  |  | Cranckase heater | 131
Bin calculation
Condition | Bin | Outdoor air temperature | Hours | Part load ratio | Heat load | Heat load covered by the heat pump |  | Electric back up heater | Annual heating demand | Annual electricity consumption with electrical back up heater
| j | Tj | hj | pl(Tj) | Ph(Tj) |  | COPbin(Tj) | elbu(Tj) | hj * Ph(Tj) | hj*((Ph(Tj)-elbu(Tj))/ COPbin(Tj))+elbu(Tj))
| - | °C | - | % | kW | kW
| 9 | -22 | 1
| 10 | -21 | 6
| 11 | -20 | 13
| 12 | -19 | 17
| 13 | -18 | 19
| 14 | -17 | 26
| 15 | -16 | 39
G | 16 | -15 | 41
| 17 | -14 | 35
| 18 | -13 | 52
| 19 | -12 | 37
| 20 | -11 | 41
| 21 | -10 | 43
| 22 | -9 | 54
| 23 | -8 | 90
A | 24 | -7 | 125
| 25 | -6 | 169
| 26 | -5 | 195
| 27 | -4 | 278
| 28 | -3 | 306
| 29 | -2 | 454
| 30 | -1 | 385
| 31 | 0 | 490
| 32 | 1 | 533
B | 33 | 2 | 380
| 34 | 3 | 228
| 35 | 4 | 261
| 36 | 5 | 279
| 37 | 6 | 229
C | 38 | 7 | 269
| 39 | 8 | 233
| 40 | 9 | 230
| 41 | 10 | 243
| 42 | 11 | 191
D | 43 | 12 | 146
| 44 | 13 | 150
| 45 | 14 | 97
| 46 | 15 | 61
6446
Calculate
Reset

## SEER air-air
Calculation of energy efficiency of air-cooled air conditioners
Product designation |  |  | Reference conditions
Manufacturer |  |  | Climate | average
Product reference |  |  | Tdesignc | 35 | °C
Type of heat pump | air-to-air |  | Pdesignc |  | kW
Operating mode | cooling only |  | HCE | 350 | hours |  | Energy Efficiency
Capacity control | fixed |  | QC |  | kWh |  | SEERon | SEER | QCE (kWh)
Performance data
Condition | Outdoor air T°C | Part load ratio (%) | Part Load (kW) | Declared Capacity (kW) | Declared EERd | Cdc | CR | EERbin
A | 35 | [8 empty] | 10
B | 30 | [8 empty] | 10
C | 25 | [8 empty] | 10
D | 20 | [8 empty] | 10
Auxiliairy power consumptions
Operating modes for cooling only
| Hours | Power input (W) | P * h (kWh) |  |  | Hours | Power input (W) | P * h (kWh)
Thermostat off | 221 |  |  |  | Thermostat off | 221
Stand by | 2142 |  |  |  | Stand by | 2142
Off mode | 5088 |  |  |  | Off mode | 0
Cranckase heater | 7760 |  |  |  | Cranckase heater | 2672
Bin calculation
Condition | Bin | Outdoor air temp. | Hours | Part load ratio | Cooling demand (kW) | Cooling capacity of the heat pump | EER | Annual cooling demand | Annual electricity consumption
| j |  |  |  | Pc(Tj) |  |  | hj*Pc(Tj) | hj*(Pc(Tj)/EER(Tj)
- | - | °C | - | % | kW | kW | - | kWh | kWh
| 1 | 17 | 205
| 2 | 18 | 227
| 3 | 19 | 225
D | 4 | 20 | 225
| 5 | 21 | 216
| 6 | 22 | 215
| 7 | 23 | 218
| 8 | 24 | 197
C | 9 | 25 | 178
| 10 | 26 | 158
| 11 | 27 | 137
| 12 | 28 | 109
| 13 | 29 | 88
B | 14 | 30 | 63
| 15 | 31 | 39
| 16 | 32 | 31
| 17 | 33 | 24
| 18 | 34 | 17
A | 19 | 35 | 13
| 20 | 36 | 9
| 21 | 37 | 4
| 22 | 38 | 3
| 23 | 39 | 1
| 24 | 40 | 0
2602
Calculate
Reset